## OctSheet-STI
SAMPLE - Sound System Speech Intelligibility (EAW QX)
|  |  | Rating/Broadband/Input |  |  | Octave Band Centre Frequency, Hz
Item / Description |  |  | STI | dB | dB(A) | 31.5 | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k
Tier 01- South | Row | Seat no.
102a | K | 30 | 0.55
102b | X | 29 | 0.45
105 | V | 4 | 0.49
109 | A | 8 | 0.54
112 | TRACK | - | 0.54
114 | TRACK | - | 0.49
117 | A | 46 | 0.54
119 | TRACK | - | 0.56
123 | TRACK | - | 0.54
Tier 01- North
127 | TRACK | - | 0.54
132 | TRACK | - | 0.54
134 | B | 35 | 0.59
137 | TRACK | - | 0.58
139 | TRACK | - | 0.53
142 | C | 31 | 0.57
144 | TRACK | - | 0.57
145 | Y | 15 | 0.4
149a | X | 14 | 0.46
149b | J | 8 | 0.53
Tier 04- South
405 | A | 1 | 0.46
409 | A | 11 | 0.46
412 | A | 39 | 0.47
414 | A | 34 | 0.46
416 | A | 37 | 0.47
421 | A | 22 | 0.51
423 | L | 21 | 0.52
Tier 04- North
423 | L | 11 | 0.52
425 | L | 27 | 0.57
431 | A | 5 | 0.43
435 | A | 5 | 0.49
437 | G | 8 | 0.5
439 | A | 10 | 0.38
442 | A | 29 | 0.47
445 | A | 21 | 0.53
Tier 06- South
608 | A | 1 | 0.52
609 | K | 51 | 0.64
611 | M | 39 | 0.6
613 | M | 40 | 0.55
615 | A | 44 | 0.58
617 | M | 40 | 0.63
619 | B | 33 | 0.53
Tier 06- North
632 | A | 39 | 0.53
634 | M | 45 | 0.57
636 | M | 36 | 0.57
638 | M | 46 | 0.54
640 | M | 43 | 0.59
642 | M | 37 | 0.61
644 | A | 35 | 0.51
Summary
Stands Only |  |  | #REF! | > 0.5 STI
All Areas (Stands + Pool) |  |  | #REF! | > 0.5 STI
Strutt Version 5.20.09aE (Smew) | [13 empty] | #ERROR!
Note on M4: 01 11 Oct 2020 03:27:16 TSW 00 11 Oct 2020 03:16:09 TSW

## OctSheet-Leq
SAMPLE - Sound System Frequency Response (EAW QX)
|  |  | Specification Limits |  |  | Octave Band Centre Frequency, Hz
Item / Description |  |  | 125-8k ± 5 dB | 2k (All) ± 3 dB | dB(A) | 31.5 | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k
Tier 1 - South | Row | Seat no.
102a | K | 30 | N | Y | 87.7872 |  |  | 83.3 | 85.7 | 83.3 | 82.1 | 80.5 | 80.2 | 37.6
102b | X | 29 | N | Y | 86.3 |  |  | 82.6 | 84.5 | 82 | 80.4 | 78.9 | 78.6 | 67.3
105 | V | 4 | N | Y | 89.0008 |  |  | 84.3 | 86.3 | 84 | 84 | 80.8 | 81.2 | 76.3
109 | A | 8 | N | Y | 89.6351 |  |  | 84.4 | 87 | 86 | 83.2 | 82.2 | 81.8 | 76.5
112 | TRACK | - | N | Y | 89.548 |  |  | 84.8 | 87.7 | 86.8 | 82.3 | 82.4 | 80.8 | 76.3
114 | TRACK | - | N | Y | 89.1502 |  |  | 86.5 | 88.6 | 86.1 | 82.3 | 80.7 | 79.7 | 79.8
116 | A | 46 | N | Y | 89.9401 |  |  | 85.1 | 89.5 | 87.1 | 82.7 | 82 | 81 | 78.6
119 | TRACK | - | N | Y | 89.3992 |  |  | 85 | 88.1 | 85.3 | 82.3 | 81.8 | 81.5 | 79.2
123 | TRACK | - | N | Y | 90.244 |  |  | 85.3 | 87.2 | 86.4 | 83.8 | 82.7 | 82.5 | 78.8
Tier- North
128 | TRACK | - | N | Y | 89.6088 |  |  | 83.5 | 87.8 | 85.9 | 83.5 | 82.1 | 81.4 | 75.5
132 | TRACK | - | N | Y | 90.2669 |  |  | 87.1 | 88.8 | 87.5 | 83.9 | 81.7 | 82.2 | 75.5
134 | B | 35 | N | Y | 90.2458 |  |  | 87.1 | 88.8 | 87.5 | 83.9 | 81.7 | 82.2 | 74.6
137 | TRACK | - | N | Y | 90.4954 |  |  | 86.3 | 89.4 | 87.7 | 83.6 | 83.1 | 81.8 | 74
139 | TRACK | - | N | Y | 90.3726 |  |  | 84.9 | 88.7 | 88 | 84.6 | 81.9 | 81.1 | 74.7
141 | C | 31 | N | Y | 90.196 |  |  | 86.5 | 89.6 | 86.3 | 83.3 | 82.8 | 82.4 | 74.4
144 | TRACK | - | N | Y | 89.3883 |  |  | 83.9 | 87.1 | 85.3 | 82.3 | 82.7 | 81.6 | 76.2
145 | Y | 15 | N | Y | 88.3859 |  |  | 85.4 | 87 | 84.3 | 81.6 | 81 | 80.2 | 77.2
149a | X | 14 | N | Y | 81.3169 |  |  | 75.9 | 79 | 76.4 | 74 | 71.6 | 72.1 | 76.9
149b | J | 8 | N | Y | 88.2783 |  |  | 84.1 | 86.3 | 84.4 | 82.1 | 80.2 | 80.2 | 77.5
Tier 4 - South
405 | A | 1 | N | Y | 88.9297 |  |  | 84.8 | 85.8 | 83.7 | 83 | 82.1 | 81.2 | 75.9
409 | A | 11 | N | Y | 88.9985 |  |  | 84.1 | 85.7 | 84.4 | 83.5 | 81.7 | 80.9 | 76
412 | A | 44 | N | Y | 88.9096 |  |  | 83.7 | 85.5 | 84.8 | 83.9 | 81.5 | 79.9 | 74.9
414 | A | 34 | N | Y | 89.1309 |  |  | 84.5 | 85.9 | 84.9 | 83.6 | 82 | 80.6 | 75.5
416 | A | 37 | N | Y | 88.706 |  |  | 85.6 | 86.2 | 84.2 | 83.2 | 81.5 | 80.3 | 74.1
421 | A | 22 | N | Y | 89.4285 |  |  | 85.3 | 86.5 | 84.6 | 84 | 81.6 | 81.7 | 77.2
423a | L | 21 | N | Y | 89.9636 |  |  | 84 | 85.7 | 86.4 | 84.3 | 82.5 | 81.7 | 76.6
Tier 4 - North
423b | L | 11 | Y | Y | 89.2172 |  |  | 84.6 | 85.1 | 85.1 | 83.2 | 82.2 | 81.3 | 76
425 | L | 27 | N | Y | 90.4168 |  |  | 85.4 | 89 | 86.7 | 83.6 | 83.1 | 82.4 | 77.3
431 | A | 5 | N | Y | 89.7298 |  |  | 83.5 | 88 | 85.5 | 84.1 | 82.2 | 81.3 | 76.1
435 | A | 5 | N | Y | 88.632 |  |  | 85.4 | 86 | 83.7 | 82.8 | 81.6 | 80.7 | 75.1
437 | G | 8 | N | Y | 88.3211 |  |  | 84.7 | 85.1 | 83.9 | 83.2 | 80.9 | 79.7 | 74.4
439 | A | 10 | Y | Y | 88.1873 |  |  | 84.8 | 84.9 | 84 | 82.4 | 81 | 79.9 | 75.2
442 | A | 29 | N | Y | 89.0488 |  |  | 84.4 | 87.7 | 84.6 | 82.1 | 81.6 | 81.9 | 75.8
445 | A | 21 | N | Y | 87.8379 |  |  | 84.6 | 86.5 | 83.7 | 82.2 | 80.2 | 79.2 | 73.7
Tier 6- South
608 | A | 1 | N | Y | 88.3093 |  |  | 82.7 | 85.8 | 83.9 | 82.8 | 81.1 | 79.8 | 74.6
609 | K | 51 | N | Y | 89.8738 |  |  | 83.9 | 86.5 | 86.3 | 84.4 | 82.2 | 81.3 | 76.6
611 | M | 39 | N | Y | 88.3567 |  |  | 83.2 | 85.4 | 85.1 | 82.7 | 80.9 | 79.4 | 73.9
613 | M | 40 | N | Y | 88.1088 |  |  | 83.4 | 84.8 | 84.6 | 83 | 80.6 | 78.8 | 73
615 | A | 44 | Y | Y | 89.5376 |  |  | 86.1 | 86.4 | 85.6 | 83.9 | 81.7 | 81.4 | 77.2
617 | M | 40 | N | Y | 89.3858 |  |  | 84 | 86.6 | 85.5 | 83.6 | 82 | 81.1 | 75.7
619 | B | 33 | N | Y | 87.6749 |  |  | 85.2 | 84.3 | 83.7 | 82 | 80.4 | 79.3 | 73.6
Tier 6- North
632 | A | 39 | N | Y | 88.097 |  |  | 84.7 | 85.6 | 84.4 | 82.1 | 80.5 | 79.8 | 75.2
634 | M | 45 | N | Y | 88.53 |  |  | 84.3 | 86 | 84.9 | 82.7 | 81 | 79.9 | 75.6
636 | M | 36 | N | Y | 90.8129 |  |  | 83.7 | 85.4 | 86.1 | 85.5 | 83.8 | 82.9 | 77.2
638 | M | 46 | N | Y | 87.8289 |  |  | 83.2 | 84.7 | 84.7 | 82.3 | 80.3 | 78.8 | 72.2
640 | M | 43 | N | Y | 87.082 |  |  | 85.2 | 85.9 | 82.8 | 81.6 | 79.3 | 78.3 | 73.1
642 | M | 37 | N | Y | 87.8746 |  |  | 83.6 | 86.4 | 84.2 | 82.4 | 79.9 | 78.9 | 74.3
644 | A | 35 | N | Y | 87.5731 |  |  | 84.5 | 85.1 | 83.9 | 81.9 | 79.9 | 78.9 | 74.4
Note on M4: 04 27 Oct 2020 11:58:52 TSW 03 27 Oct 2020 11:40:00 TSW 02 11 Oct 2020 03:27:28 TSW 01 11 Oct 2020 02:27:16 TSW 00 11 Oct 2020 02:23:43 TSW

## Formatted RTA for comparison
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000 | Minus 5 | Average | Plus 5 | 125 | 250 | 500 | 1k | 2k | 4k | 8k | ALL | Minus 3 | 2k Average | Plus 3 | 2k | ALL
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
Section | db
102a | LZeq | 60.4 | 57.3 | 74.8 | 82.1 | 83.3 | 85.7 | 83.3 | 82.1 | 80.5 | 80.2 | 75.4 | 68.6 | 74.35 | 79.35 | 84.35 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 | #NAME? | 81.2708 | #NAME? | #NAME? | 0
102b | LZeq | 62.5 | 58.9 | 72.4 | 81.3 | 82.6 | 84.5 | 82 | 80.4 | 78.9 | 78.6 | 73.6 | 65.3 | 73.1 | 78.1 | 83.1 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
105 | LZeq | 62 | 59 | 74.2 | 80.1 | 84.3 | 86.3 | 84 | 84 | 80.8 | 81.2 | 75.9 | 71.3 | 75.1 | 80.1 | 85.1 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
109 | LZeq | 64.4 | 61.1 | 75.8 | 81.7 | 84.4 | 87 | 86 | 83.2 | 82.2 | 81.8 | 77.4 | 70.5 | 75.9 | 80.9 | 85.9 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
112 | LZeq | 69.9 | 66.7 | 75.7 | 82.9 | 84.8 | 87.7 | 86.8 | 82.3 | 82.4 | 80.8 | 76.1 | 69.7 | 75.45 | 80.45 | 85.45 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
114 | LZeq | 73.2 | 71 | 74.2 | 83 | 86.5 | 88.6 | 86.1 | 82.3 | 80.7 | 79.7 | 74 | 66.7 | 75.25 | 80.25 | 85.25 | FAIL | FAIL | FAIL | PASS | PASS | PASS | FAIL | 4 |  |  |  | #NAME? | 0
116 | LZeq | 62 | 60 | 75.3 | 83.8 | 85.1 | 89.5 | 87.1 | 82.7 | 82 | 81 | 76.6 | 69.5 | 75.85 | 80.85 | 85.85 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
119 | LZeq | 64.2 | 61.9 | 76.3 | 82.6 | 85 | 88.1 | 85.3 | 82.3 | 81.8 | 81.5 | 76.1 | 71.4 | 75.55 | 80.55 | 85.55 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
123 | LZeq | 66.9 | 63.7 | 75.2 | 82 | 85.3 | 87.2 | 86.4 | 83.8 | 82.7 | 82.5 | 77.8 | 71.7 | 76.55 | 81.55 | 86.55 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
128 | LZeq | 62.6 | 60.8 | 75.4 | 83.8 | 83.5 | 87.8 | 85.9 | 83.5 | 82.1 | 81.4 | 75.6 | 71.2 | 74.55 | 79.55 | 84.55 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
132 | LZeq | 66.3 | 63.7 | 74.2 | 81.5 | 84.9 | 88.4 | 85.2 | 82.9 | 82.6 | 81.2 | 75.7 | 71.5 | 75.3 | 80.3 | 85.3 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
134 | LZeq | 74.4 | 70.4 | 76 | 81.7 | 87.1 | 88.8 | 87.5 | 83.9 | 81.7 | 82.2 | 76.8 | 71 | 76.95 | 81.95 | 86.95 | FAIL | FAIL | FAIL | PASS | PASS | PASS | FAIL | 4 |  |  |  | #NAME? | 0
137 | LZeq | 67.9 | 66 | 74.2 | 83.5 | 86.3 | 89.4 | 87.7 | 83.6 | 83.1 | 81.8 | 76.9 | 70.9 | 76.6 | 81.6 | 86.6 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
139 | LZeq | 61.4 | 59.4 | 72 | 82 | 84.9 | 88.7 | 88 | 84.6 | 81.9 | 81.1 | 77.9 | 71.2 | 76.4 | 81.4 | 86.4 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
141 | LZeq | 59.1 | 58 | 76.6 | 82.3 | 86.5 | 89.6 | 86.3 | 83.3 | 82.8 | 82.4 | 77.5 | 72.4 | 77 | 82 | 87 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
144 | LZeq | 66.5 | 62.7 | 75.1 | 83.5 | 83.9 | 87.1 | 85.3 | 82.3 | 82.7 | 81.6 | 76.2 | 72.6 | 75.05 | 80.05 | 85.05 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
145 | LZeq | 57.7 | 56.4 | 74.1 | 82.3 | 85.4 | 87 | 84.3 | 81.6 | 81 | 80.2 | 74.5 | 69.2 | 74.95 | 79.95 | 84.95 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
149a | LZeq | 65 | 60.4 | 67.7 | 75.7 | 75.9 | 79 | 76.4 | 74 | 71.6 | 72.1 | 67 | 57.1 | 66.45 | 71.45 | 76.45 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
149b | LZeq | 57.9 | 56 | 74.2 | 81.7 | 84.1 | 86.3 | 84.4 | 82.1 | 80.2 | 80.2 | 74.3 | 68.2 | 74.2 | 79.2 | 84.2 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
405 | LZeq | 62.6 | 59.4 | 76.6 | 83 | 84.8 | 85.8 | 83.7 | 83 | 82.1 | 81.2 | 75.9 | 71.6 | 75.35 | 80.35 | 85.35 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
409 | LZeq | 72.3 | 68.2 | 77.2 | 82.7 | 84.1 | 85.7 | 84.4 | 83.5 | 81.7 | 80.9 | 76 | 69 | 75.05 | 80.05 | 85.05 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
412 | LZeq | 71.1 | 66 | 77.5 | 83.7 | 83.7 | 85.5 | 84.8 | 83.9 | 81.5 | 79.9 | 74.9 | 68.2 | 74.3 | 79.3 | 84.3 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
414 | LZeq | 61.1 | 57 | 76.3 | 83 | 84.5 | 85.9 | 84.9 | 83.6 | 82 | 80.6 | 75.5 | 68.5 | 75 | 80 | 85 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
416 | LZeq | 65.5 | 63.2 | 76.2 | 84.2 | 85.6 | 86.2 | 84.2 | 83.2 | 81.5 | 80.3 | 74.1 | 66.3 | 74.85 | 79.85 | 84.85 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
421 | LZeq | 60 | 56.9 | 75.9 | 82.2 | 85.3 | 86.5 | 84.6 | 84 | 81.6 | 81.7 | 77.2 | 69.7 | 76.25 | 81.25 | 86.25 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
423a | LZeq | 58.3 | 58.2 | 72.8 | 82.6 | 84 | 85.7 | 86.4 | 84.3 | 82.5 | 81.7 | 76.6 | 70.7 | 75.3 | 80.3 | 85.3 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
423b | LZeq | 56.7 | 57.8 | 73.6 | 82.3 | 84.6 | 85.1 | 85.1 | 83.2 | 82.2 | 81.3 | 76 | 70.4 | 75.3 | 80.3 | 85.3 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 |  |  |  | #NAME? | 0
425 | LZeq | 58.3 | 57.8 | 73 | 83.3 | 85.4 | 89 | 86.7 | 83.6 | 83.1 | 82.4 | 77.3 | 70.9 | 76.35 | 81.35 | 86.35 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
431 | LZeq | 55.6 | 57.2 | 76.9 | 83.2 | 83.5 | 88 | 85.5 | 84.1 | 82.2 | 81.3 | 76.1 | 72.1 | 74.8 | 79.8 | 84.8 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
435 | LZeq | 56.5 | 57.5 | 75.9 | 85 | 85.4 | 86 | 83.7 | 82.8 | 81.6 | 80.7 | 75.1 | 67.7 | 75.25 | 80.25 | 85.25 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
437 | LZeq | 63.6 | 61.6 | 75.6 | 83 | 84.7 | 85.1 | 83.9 | 83.2 | 80.9 | 79.7 | 74.4 | 66.3 | 74.55 | 79.55 | 84.55 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
439 | LZeq | 62.7 | 60.5 | 75.9 | 81.9 | 84.8 | 84.9 | 84 | 82.4 | 81 | 79.9 | 75.2 | 67.4 | 75 | 80 | 85 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 |  |  |  | #NAME? | 0
442 | LZeq | 60.8 | 60.9 | 77.1 | 83.5 | 84.4 | 87.7 | 84.6 | 82.1 | 81.6 | 81.9 | 75.8 | 68.1 | 75.1 | 80.1 | 85.1 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
445 | LZeq | 70.4 | 65.8 | 74.4 | 84.5 | 84.6 | 86.5 | 83.7 | 82.2 | 80.2 | 79.2 | 73.7 | 68.8 | 74.15 | 79.15 | 84.15 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
608 | LZeq | 81.1 | 80.1 | 79.3 | 84 | 82.7 | 85.8 | 83.9 | 82.8 | 81.1 | 79.8 | 74.6 | 71 | 73.65 | 78.65 | 83.65 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
609 | LZeq | 60.5 | 59.8 | 73.8 | 81 | 83.9 | 86.5 | 86.3 | 84.4 | 82.2 | 81.3 | 76.6 | 74.7 | 75.25 | 80.25 | 85.25 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
611 | LZeq | 58.6 | 59.4 | 72.6 | 82.4 | 83.2 | 85.4 | 85.1 | 82.7 | 80.9 | 79.4 | 73.9 | 70.9 | 73.55 | 78.55 | 83.55 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
613 | LZeq | 58.3 | 59.5 | 75.4 | 81.1 | 83.4 | 84.8 | 84.6 | 83 | 80.6 | 78.8 | 73 | 67.3 | 73.2 | 78.2 | 83.2 | FAIL | FAIL | FAIL | PASS | PASS | PASS | FAIL | 4 |  |  |  | #NAME? | 0
615 | LZeq | 66.2 | 63.6 | 74.4 | 83.9 | 86.1 | 86.4 | 85.6 | 83.9 | 81.7 | 81.4 | 77.2 | 68.9 | 76.65 | 81.65 | 86.65 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 |  |  |  | #NAME? | 0
617 | LZeq | 61.1 | 60.4 | 72.4 | 81.6 | 84 | 86.6 | 85.5 | 83.6 | 82 | 81.1 | 75.7 | 73 | 74.85 | 79.85 | 84.85 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
619 | LZeq | 56.5 | 57.2 | 74.2 | 86.3 | 85.2 | 84.3 | 83.7 | 82 | 80.4 | 79.3 | 73.6 | 68.8 | 74.4 | 79.4 | 84.4 | FAIL | PASS | PASS | PASS | PASS | PASS | FAIL | 2 |  |  |  | #NAME? | 0
632 | LZeq | 63.2 | 58.8 | 75.9 | 86 | 84.7 | 85.6 | 84.4 | 82.1 | 80.5 | 79.8 | 75.2 | 68.8 | 74.95 | 79.95 | 84.95 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
634 | LZeq | 65.8 | 63.1 | 73.5 | 82.4 | 84.3 | 86 | 84.9 | 82.7 | 81 | 79.9 | 75.6 | 68.9 | 74.95 | 79.95 | 84.95 | PASS | FAIL | PASS | PASS | PASS | PASS | PASS | 1 |  |  |  | #NAME? | 0
636 | LZeq | 64.1 | 64.9 | 74.9 | 81.5 | 83.7 | 85.4 | 86.1 | 85.5 | 83.8 | 82.9 | 77.2 | 75.5 | 75.45 | 80.45 | 85.45 | PASS | PASS | FAIL | FAIL | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
638 | LZeq | 61.8 | 60.6 | 73.4 | 80.8 | 83.2 | 84.7 | 84.7 | 82.3 | 80.3 | 78.8 | 72.2 | 67.7 | 72.7 | 77.7 | 82.7 | FAIL | FAIL | FAIL | PASS | PASS | PASS | FAIL | 4 |  |  |  | #NAME? | 0
640 | LZeq | 57.9 | 60.2 | 72.9 | 82 | 85.2 | 85.9 | 82.8 | 81.6 | 79.3 | 78.3 | 73.1 | 65 | 74.15 | 79.15 | 84.15 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0
642 | LZeq | 62.7 | 63.6 | 75.1 | 83 | 83.6 | 86.4 | 84.2 | 82.4 | 79.9 | 78.9 | 74.3 | 66.4 | 73.95 | 78.95 | 83.95 | PASS | FAIL | FAIL | PASS | PASS | PASS | PASS | 2 |  |  |  | #NAME? | 0
644 | LZeq | 61.2 | 60 | 74.7 | 84.7 | 84.5 | 85.1 | 83.9 | 81.9 | 79.9 | 78.9 | 74.4 | 67.5 | 74.45 | 79.45 | 84.45 | FAIL | FAIL | PASS | PASS | PASS | PASS | FAIL | 3 |  |  |  | #NAME? | 0

## Level 1 RTA RAW
XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\102K30RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:44:26
| End: | 2020-12-17, 22:44:36
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 67.2 | 63.9 | 79.4 | 85.8 | 85.7 | 87.8 | 84.9 | 83.2 | 81.4 | 81.4 | 76.5 | 71
| LZFmin | 52.2 | 49.4 | 69.9 | 77.7 | 80.9 | 83.7 | 81.9 | 80.7 | 79.7 | 79.2 | 73.8 | 66.2
| LZeq | 60.4 | 57.3 | 74.8 | 82.1 | 83.3 | 85.7 | 83.3 | 82.1 | 80.5 | 80.2 | 75.4 | 68.6
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| EBE97A5129529B24B93C1EB396CEB1A4XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\102X29RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:43:34
| End: | 2020-12-17, 22:43:44
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 71.3 | 66.4 | 76.1 | 86.1 | 85.9 | 86.2 | 83.5 | 81.8 | 80 | 79.4 | 75.2 | 67.4
| LZFmin | 54.9 | 49 | 66.6 | 77.6 | 79 | 82.5 | 80.5 | 79 | 77.5 | 77.7 | 72.1 | 62.5
| LZeq | 62.5 | 58.9 | 72.4 | 81.3 | 82.6 | 84.5 | 82 | 80.4 | 78.9 | 78.6 | 73.6 | 65.3
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 4AC814A9CD3BD0529781A4E86D6ED1D8XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\105V4RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:45:10
| End: | 2020-12-17, 22:45:20
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68.9 | 66.1 | 78.1 | 83.5 | 86.5 | 88.3 | 85.4 | 85.1 | 81.9 | 82.3 | 77.9 | 74.5
| LZFmin | 50.3 | 50.3 | 68.5 | 75.7 | 81.4 | 84.2 | 82.6 | 82.6 | 80 | 79.8 | 74 | 68
| LZeq | 62 | 59 | 74.2 | 80.1 | 84.3 | 86.3 | 84 | 84 | 80.8 | 81.2 | 75.9 | 71.3
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 52C97147A5F07B2663BE98C17370C632XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\109A8RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:46:50
| End: | 2020-12-17, 22:47:00
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 71.2 | 70.3 | 80 | 86.4 | 86.7 | 90 | 87.8 | 84.6 | 83.2 | 82.8 | 79.7 | 74.6
| LZFmin | 52.7 | 53.2 | 70.2 | 77.3 | 81.3 | 84.6 | 84.5 | 82 | 81.4 | 80.9 | 76 | 68.2
| LZeq | 64.4 | 61.1 | 75.8 | 81.7 | 84.4 | 87 | 86 | 83.2 | 82.2 | 81.8 | 77.4 | 70.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 594D50E3E3470A77B8DCF6DC7E13C4ADXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\112RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:34:06
| End: | 2020-12-17, 22:34:16
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 79.7 | 78.6 | 80.6 | 85.5 | 86.8 | 89.7 | 88.4 | 83.3 | 83.4 | 81.5 | 77.4 | 71.7
| LZFmin | 50.3 | 51.3 | 70.2 | 79.5 | 82.6 | 85.8 | 84.9 | 80.9 | 81.4 | 80 | 74.9 | 67.8
| LZeq | 69.9 | 66.7 | 75.7 | 82.9 | 84.8 | 87.7 | 86.8 | 82.3 | 82.4 | 80.8 | 76.1 | 69.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| FFA4C743FEC0C21307F96C2E6F7434EEXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\114RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:33:32
| End: | 2020-12-17, 22:33:42
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 82 | 80 | 78 | 86.7 | 89.3 | 90.9 | 87.6 | 83.3 | 81.3 | 80.8 | 75.2 | 68.5
| LZFmin | 58.4 | 54.6 | 68.3 | 77.8 | 83.3 | 86.9 | 84.5 | 81.3 | 80 | 78.8 | 72.7 | 64.5
| LZeq | 73.2 | 71 | 74.2 | 83 | 86.5 | 88.6 | 86.1 | 82.3 | 80.7 | 79.7 | 74 | 66.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| FD870387BA8986A7A2E45FDE1327F10FXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\116A46RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:48:12
| End: | 2020-12-17, 22:48:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 66.9 | 65.1 | 80.5 | 87.5 | 88.7 | 91.5 | 89.3 | 84.2 | 82.9 | 82 | 77.7 | 71
| LZFmin | 55.9 | 51.7 | 69.3 | 79.4 | 82.2 | 87.5 | 85.6 | 81.5 | 81 | 79.9 | 75 | 66.4
| LZeq | 62 | 60 | 75.3 | 83.8 | 85.1 | 89.5 | 87.1 | 82.7 | 82 | 81 | 76.6 | 69.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 187E34E2DE3B9F9B66B9AF1F98B3BF2DXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\119RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:32:28
| End: | 2020-12-17, 22:32:38
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73.2 | 73.4 | 80.3 | 85.9 | 87.4 | 89.9 | 87.9 | 83.5 | 83.1 | 82.5 | 77.3 | 75.2
| LZFmin | 50.7 | 51.1 | 70.2 | 79.3 | 82.5 | 86.3 | 83.3 | 81.1 | 80.5 | 80.4 | 74.9 | 67.7
| LZeq | 64.2 | 61.9 | 76.3 | 82.6 | 85 | 88.1 | 85.3 | 82.3 | 81.8 | 81.5 | 76.1 | 71.4
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 967A28CE1326D8AA32D7EF0F86D87A03XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\123RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:31:40
| End: | 2020-12-17, 22:31:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 74.1 | 70.5 | 80.6 | 86 | 87.4 | 88.9 | 88 | 85 | 84 | 83.9 | 79.5 | 74.7
| LZFmin | 56.2 | 53.7 | 69.3 | 76.9 | 82.9 | 85.1 | 84.9 | 82.7 | 81.7 | 81.4 | 76.4 | 68.4
| LZeq | 66.9 | 63.7 | 75.2 | 82 | 85.3 | 87.2 | 86.4 | 83.8 | 82.7 | 82.5 | 77.8 | 71.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| CE7AAD0F89AA9921E682D548E7DCADDDXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\128RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:30:40
| End: | 2020-12-17, 22:30:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 69.3 | 66.2 | 79.9 | 88 | 85.6 | 90 | 87.5 | 84.6 | 83.1 | 82.2 | 76.7 | 73.5
| LZFmin | 51 | 53 | 69.2 | 79.7 | 81.1 | 86 | 84.1 | 82.6 | 81.2 | 80.5 | 74.5 | 69.2
| LZeq | 62.6 | 60.8 | 75.4 | 83.8 | 83.5 | 87.8 | 85.9 | 83.5 | 82.1 | 81.4 | 75.6 | 71.2
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| B67C827D6025F3E4BDCFAABEAB184765XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\132RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:29:50
| End: | 2020-12-17, 22:30:00
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73.5 | 70.6 | 78.6 | 84.6 | 87.5 | 90.6 | 87 | 84 | 83.5 | 82.1 | 76.6 | 73.7
| LZFmin | 56.3 | 55.9 | 67.9 | 78.4 | 82.5 | 86.8 | 83.4 | 82 | 81.6 | 80.1 | 74.6 | 69.2
| LZeq | 66.3 | 63.7 | 74.2 | 81.5 | 84.9 | 88.4 | 85.2 | 82.9 | 82.6 | 81.2 | 75.7 | 71.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 2AA24FB1B533129BA8A44F25E8FE1F7EXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\134B35RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:26:20
| End: | 2020-12-17, 23:26:30
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 83.6 | 76.7 | 80.3 | 85.1 | 90.4 | 90.3 | 88.9 | 84.7 | 82.6 | 83 | 77.6 | 72.1
| LZFmin | 62.3 | 59.4 | 70.2 | 78 | 83.2 | 87.1 | 85.6 | 82.8 | 81 | 81.4 | 75.9 | 69.9
| LZeq | 74.4 | 70.4 | 76 | 81.7 | 87.1 | 88.8 | 87.5 | 83.9 | 81.7 | 82.2 | 76.8 | 71
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| F486E5A88E63990006E4D0CF28F2D9C7XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\137RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:28:36
| End: | 2020-12-17, 22:28:46
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 75.8 | 71.8 | 79 | 86.6 | 88.9 | 91.6 | 89.4 | 84.7 | 84 | 83.1 | 77.9 | 72.7
| LZFmin | 57.4 | 57.7 | 70.3 | 78.2 | 83.6 | 87.4 | 86.1 | 82.7 | 82.2 | 81 | 75.9 | 69.7
| LZeq | 67.9 | 66 | 74.2 | 83.5 | 86.3 | 89.4 | 87.7 | 83.6 | 83.1 | 81.8 | 76.9 | 70.9
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 1DC9DA213F69499E5D7AB71328D8EAE0XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\139RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:27:56
| End: | 2020-12-17, 22:28:06
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 70.7 | 65 | 76.7 | 84.8 | 87 | 90.4 | 89.7 | 85.5 | 82.7 | 81.9 | 79.1 | 73
| LZFmin | 53.6 | 51.9 | 66.5 | 76.9 | 82.3 | 86.7 | 86.2 | 83.5 | 80.9 | 80.3 | 76.9 | 69.9
| LZeq | 61.4 | 59.4 | 72 | 82 | 84.9 | 88.7 | 88 | 84.6 | 81.9 | 81.1 | 77.9 | 71.2
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| CDB9B90E269235705D538E459BA14D28XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\141C31RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:24:14
| End: | 2020-12-17, 23:24:24
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 65.6 | 64.6 | 80.5 | 85.4 | 88.8 | 91.5 | 87.5 | 84.6 | 84 | 83.4 | 78.4 | 74.2
| LZFmin | 50.7 | 51.3 | 71.5 | 78 | 84.4 | 87.9 | 84.9 | 82.4 | 81.7 | 81.5 | 76.7 | 70.3
| LZeq | 59.1 | 58 | 76.6 | 82.3 | 86.5 | 89.6 | 86.3 | 83.3 | 82.8 | 82.4 | 77.5 | 72.4
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| A7211D7BC920C0EE1CCEDFB73EE52EA2XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\144RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:22:20
| End: | 2020-12-17, 22:22:30
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 78.3 | 71.4 | 78.8 | 86.5 | 86.7 | 89.1 | 86.8 | 83.8 | 83.8 | 82.9 | 77.8 | 75.3
| LZFmin | 51.3 | 50.8 | 70.9 | 79.7 | 80.8 | 85.1 | 83.7 | 81.4 | 81.6 | 80.4 | 74.6 | 69.3
| LZeq | 66.5 | 62.7 | 75.1 | 83.5 | 83.9 | 87.1 | 85.3 | 82.3 | 82.7 | 81.6 | 76.2 | 72.6
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| E3D0C05E5F4D71F91872C7581AC17BBEXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\145Y15RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:22:40
| End: | 2020-12-17, 23:22:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 65.8 | 61.5 | 78.3 | 86.4 | 88.2 | 89 | 85.9 | 83.1 | 81.9 | 81.3 | 75.6 | 72.3
| LZFmin | 48 | 48.9 | 68.7 | 79.3 | 81.7 | 84.9 | 82.8 | 80.6 | 80.1 | 79.2 | 73.5 | 67.2
| LZeq | 57.7 | 56.4 | 74.1 | 82.3 | 85.4 | 87 | 84.3 | 81.6 | 81 | 80.2 | 74.5 | 69.2
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| C1279D97B02B074335B5B8BFA22BEB9DXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\149J8RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:21:40
| End: | 2020-12-17, 23:21:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 65.9 | 61.1 | 78.4 | 85.4 | 86.7 | 88.5 | 85.8 | 83.4 | 81.2 | 81.2 | 75.7 | 70.5
| LZFmin | 48.5 | 48.9 | 68 | 76.8 | 81.7 | 84 | 82.8 | 80.6 | 79.2 | 79.4 | 72.9 | 65.4
| LZeq | 57.9 | 56 | 74.2 | 81.7 | 84.1 | 86.3 | 84.4 | 82.1 | 80.2 | 80.2 | 74.3 | 68.2
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| AF30F07BE875632C3228073C598446FFXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL1-2804\149X14RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:20:40
| End: | 2020-12-17, 23:20:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73.7 | 68.6 | 77.8 | 83.5 | 83.4 | 86.6 | 83.1 | 80.5 | 78.3 | 78.4 | 73.1 | 66.6
| LZFmin | 50.1 | 51 | 52.4 | 53 | 51.2 | 49.3 | 46.6 | 44.2 | 39.1 | 33 | 24.3 | 20.9
| LZeq | 65 | 60.4 | 67.7 | 75.7 | 75.9 | 79 | 76.4 | 74 | 71.6 | 72.1 | 67 | 57.1
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
ECB1633ABA28FE8AA49357C351452DFA

## Level 4 RTA RAW
XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\405A1RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:54:12
| End: | 2020-12-17, 22:54:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 69.2 | 67.1 | 81 | 86 | 86.8 | 87.9 | 85 | 84.1 | 82.9 | 82.3 | 76.8 | 74.2
| LZFmin | 54.5 | 52.1 | 72.6 | 79 | 82.5 | 83.8 | 82.3 | 81.8 | 81.3 | 80.3 | 74.6 | 69.2
| LZeq | 62.6 | 59.4 | 76.6 | 83 | 84.8 | 85.8 | 83.7 | 83 | 82.1 | 81.2 | 75.9 | 71.6
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 261EE7773A6DFDB971E128CDE312068AXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\409A11RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:55:04
| End: | 2020-12-17, 22:55:14
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 86.2 | 81.7 | 80.8 | 86.8 | 86.6 | 88.1 | 86.3 | 84.8 | 82.7 | 81.8 | 77.6 | 72.2
| LZFmin | 53.9 | 56.2 | 71.5 | 77.8 | 81.6 | 83.8 | 82.9 | 82.5 | 80.3 | 79.9 | 74.9 | 67
| LZeq | 72.3 | 68.2 | 77.2 | 82.7 | 84.1 | 85.7 | 84.4 | 83.5 | 81.7 | 80.9 | 76 | 69
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 8924E9BF8DB4C349AEE5E580722840CCXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\412A44RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:55:54
| End: | 2020-12-17, 22:56:04
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 81 | 74.5 | 81.9 | 88.4 | 86.6 | 88 | 85.9 | 85.1 | 82.3 | 80.8 | 76.1 | 70.4
| LZFmin | 57.3 | 55.4 | 70.7 | 79 | 81.2 | 83.4 | 83.5 | 82.6 | 80.6 | 79 | 73.6 | 65.9
| LZeq | 71.1 | 66 | 77.5 | 83.7 | 83.7 | 85.5 | 84.8 | 83.9 | 81.5 | 79.9 | 74.9 | 68.2
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 7BFFA57E3E89806C1BBAA84B4D9E9F12XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\414A34RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:56:40
| End: | 2020-12-17, 22:56:50
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68 | 62.4 | 80.3 | 85.9 | 87 | 87.6 | 86 | 84.7 | 83 | 81.5 | 76.3 | 69.9
| LZFmin | 51.9 | 49.7 | 70.1 | 79.1 | 82 | 84 | 83.4 | 82.2 | 81.2 | 80 | 74.6 | 67.1
| LZeq | 61.1 | 57 | 76.3 | 83 | 84.5 | 85.9 | 84.9 | 83.6 | 82 | 80.6 | 75.5 | 68.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 962DAE666809E83748CF12C14029CC10XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\416A42RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:57:20
| End: | 2020-12-17, 22:57:30
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73 | 71.1 | 80.6 | 88.7 | 88.7 | 88.3 | 85.8 | 84.6 | 82.4 | 80.9 | 75.8 | 70.2
| LZFmin | 57.5 | 54.9 | 69.5 | 79.8 | 82.8 | 84.5 | 83 | 81.8 | 80.7 | 79.6 | 73.1 | 63.3
| LZeq | 65.5 | 63.2 | 76.2 | 84.2 | 85.6 | 86.2 | 84.2 | 83.2 | 81.5 | 80.3 | 74.1 | 66.3
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 48CE75C97C7913B0D81FA37E529CDC06XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\421A22RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:59:10
| End: | 2020-12-17, 22:59:20
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68.5 | 62.4 | 80.1 | 86.7 | 88.2 | 88.8 | 86.4 | 85.4 | 83 | 82.4 | 78.1 | 72.6
| LZFmin | 50.9 | 50.6 | 70.3 | 78.7 | 82.7 | 84.4 | 82.8 | 82.3 | 80.6 | 81.1 | 76 | 68
| LZeq | 60 | 56.9 | 75.9 | 82.2 | 85.3 | 86.5 | 84.6 | 84 | 81.6 | 81.7 | 77.2 | 69.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| B21DDA14460701C6A13497D356F99BC4XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\423L21RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:00:04
| End: | 2020-12-17, 23:00:14
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 66.2 | 61.7 | 77.7 | 86.5 | 86.5 | 87.8 | 87.8 | 85.7 | 83.8 | 82.9 | 78.4 | 73.7
| LZFmin | 49.7 | 52.3 | 67.6 | 78.2 | 81.7 | 83.9 | 84.7 | 83.1 | 81.3 | 80.7 | 75.4 | 67.9
| LZeq | 58.3 | 58.2 | 72.8 | 82.6 | 84 | 85.7 | 86.4 | 84.3 | 82.5 | 81.7 | 76.6 | 70.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| F3ED30F7C863D9471AEB7795B74D8BB9XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\423RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:04:12
| End: | 2020-12-17, 22:04:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 62.3 | 63.7 | 79.1 | 85.3 | 87.2 | 86.7 | 86.6 | 84.1 | 83.7 | 82.3 | 77.3 | 73.4
| LZFmin | 47 | 52.4 | 68 | 78.7 | 82.1 | 83.1 | 83.7 | 82.2 | 81.3 | 80.3 | 74.7 | 66.5
| LZeq | 56.7 | 57.8 | 73.6 | 82.3 | 84.6 | 85.1 | 85.1 | 83.2 | 82.2 | 81.3 | 76 | 70.4
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 29E8BA44774C93ED52A181D68563EB5AXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\425RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:06:00
| End: | 2020-12-17, 22:06:10
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 64.3 | 62.3 | 77.9 | 87 | 87.8 | 91.5 | 88.4 | 84.7 | 84.2 | 83.5 | 79 | 74.1
| LZFmin | 51.1 | 49.7 | 67.7 | 78.9 | 83 | 86.4 | 85 | 82.6 | 81.9 | 81.3 | 75.9 | 68
| LZeq | 58.3 | 57.8 | 73 | 83.3 | 85.4 | 89 | 86.7 | 83.6 | 83.1 | 82.4 | 77.3 | 70.9
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| D5F2A1C51D3C9630D1CCB1CD721BB8EDXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\431RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:08:06
| End: | 2020-12-17, 22:08:16
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 61.9 | 62 | 81.5 | 86.8 | 85.5 | 89.9 | 86.9 | 85.4 | 85.4 | 82.3 | 76.8 | 74.1
| LZFmin | 46 | 51.7 | 70.6 | 80.1 | 81.1 | 86.2 | 84 | 83.1 | 81.3 | 80.6 | 75.3 | 70.1
| LZeq | 55.6 | 57.2 | 76.9 | 83.2 | 83.5 | 88 | 85.5 | 84.1 | 82.2 | 81.3 | 76.1 | 72.1
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| F2474256D91CCCC719B44C0DD4F3F158XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\435RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:09:18
| End: | 2020-12-17, 22:09:28
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 63 | 61.5 | 79.9 | 88.7 | 88.1 | 88.4 | 84.8 | 83.8 | 82.4 | 81.2 | 75.9 | 68.9
| LZFmin | 48.8 | 52.7 | 71.5 | 80.3 | 81.9 | 84.2 | 82.3 | 81.9 | 80.8 | 80.1 | 74.2 | 66.6
| LZeq | 56.5 | 57.5 | 75.9 | 85 | 85.4 | 86 | 83.7 | 82.8 | 81.6 | 80.7 | 75.1 | 67.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| EE2655A0BAE91CA7154A8ED5822BBADCXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\437RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:10:12
| End: | 2020-12-17, 22:10:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 70.4 | 69.1 | 79.2 | 86.5 | 87.7 | 86.6 | 85.2 | 84.4 | 81.9 | 80.4 | 75.4 | 67.8
| LZFmin | 52.2 | 55.1 | 70.4 | 79.1 | 82 | 83.4 | 82 | 82 | 79.9 | 78.8 | 73.7 | 65.2
| LZeq | 63.6 | 61.6 | 75.6 | 83 | 84.7 | 85.1 | 83.9 | 83.2 | 80.9 | 79.7 | 74.4 | 66.3
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| EDC05EBF09AD8E000B4713727374B7F5XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\439RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:11:16
| End: | 2020-12-17, 22:11:26
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 70.7 | 67.4 | 81.2 | 85.3 | 87.5 | 86.6 | 85.1 | 83.7 | 81.9 | 80.7 | 76.4 | 69.1
| LZFmin | 54.8 | 52.9 | 69.4 | 78.2 | 81.4 | 83 | 82.6 | 81.2 | 80 | 79 | 74.3 | 66
| LZeq | 62.7 | 60.5 | 75.9 | 81.9 | 84.8 | 84.9 | 84 | 82.4 | 81 | 79.9 | 75.2 | 67.4
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 95B6CB2E74B629A64B3EE3FECEFF7004XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\442RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:12:20
| End: | 2020-12-17, 22:12:30
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68.4 | 66.8 | 81 | 86.7 | 86.8 | 89.5 | 86.4 | 83 | 82.4 | 82.8 | 76.9 | 69.3
| LZFmin | 49.5 | 53.7 | 70.4 | 79.4 | 82 | 85.5 | 83.3 | 81.1 | 80.7 | 81.1 | 74.9 | 66.7
| LZeq | 60.8 | 60.9 | 77.1 | 83.5 | 84.4 | 87.7 | 84.6 | 82.1 | 81.6 | 81.9 | 75.8 | 68.1
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 404CB5CB3F40825A1D6DF37137D108DAXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL4-2804\445RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 22:13:18
| End: | 2020-12-17, 22:13:28
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 81 | 72.8 | 79.7 | 88 | 87.4 | 88.1 | 85.1 | 83.3 | 81 | 80.3 | 74.6 | 71.1
| LZFmin | 53.7 | 53.3 | 67.6 | 80.8 | 82 | 84.3 | 82.1 | 81.3 | 79.5 | 78.2 | 72.5 | 65.8
| LZeq | 70.4 | 65.8 | 74.4 | 84.5 | 84.6 | 86.5 | 83.7 | 82.2 | 80.2 | 79.2 | 73.7 | 68.8
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
44609AD081CE8A7C2B8CDB3BDEC75100

## Level 6 RTA RAW
XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\608A1RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:08:38
| End: | 2020-12-17, 23:08:48
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 88.5 | 90.5 | 86.1 | 87.7 | 84.8 | 87.5 | 85.2 | 83.8 | 81.9 | 80.8 | 75.5 | 73.5
| LZFmin | 64.5 | 67.6 | 73.3 | 80.3 | 79.9 | 84.5 | 82.6 | 81.4 | 80.2 | 79 | 73.5 | 67.7
| LZeq | 81.1 | 80.1 | 79.3 | 84 | 82.7 | 85.8 | 83.9 | 82.8 | 81.1 | 79.8 | 74.6 | 71
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 8803DD82CE7621E7A5CC087D373307C2XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\609K51RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:09:36
| End: | 2020-12-17, 23:09:46
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 66.6 | 65.9 | 78.5 | 84.1 | 86.3 | 88.5 | 87.9 | 85.4 | 83.1 | 82 | 78.3 | 77.8
| LZFmin | 48.7 | 51.9 | 68.9 | 76.8 | 81.4 | 84.7 | 84.9 | 83.3 | 81.5 | 80.6 | 75.5 | 73
| LZeq | 60.5 | 59.8 | 73.8 | 81 | 83.9 | 86.5 | 86.3 | 84.4 | 82.2 | 81.3 | 76.6 | 74.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 3F5B8164049225193C061412F938FB73XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\611M39RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:10:18
| End: | 2020-12-17, 23:10:28
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 64.8 | 64.8 | 76.5 | 85.3 | 87 | 87.4 | 86.6 | 84.1 | 81.6 | 80 | 74.7 | 73.1
| LZFmin | 46 | 52.5 | 65.9 | 77.1 | 80 | 82.6 | 83.6 | 81.5 | 80.1 | 78.8 | 73.1 | 68.7
| LZeq | 58.6 | 59.4 | 72.6 | 82.4 | 83.2 | 85.4 | 85.1 | 82.7 | 80.9 | 79.4 | 73.9 | 70.9
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 581FC25BAC7F5321ACF3CE5327449078XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\613M39RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:11:02
| End: | 2020-12-17, 23:11:12
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 64.3 | 63.9 | 80.9 | 84.6 | 87.4 | 86.4 | 86 | 83.9 | 81.3 | 79.7 | 73.9 | 68.7
| LZFmin | 47 | 53.6 | 68.4 | 77.8 | 80.6 | 83.3 | 83.2 | 82 | 79.9 | 78.1 | 72.2 | 65.3
| LZeq | 58.3 | 59.5 | 75.4 | 81.1 | 83.4 | 84.8 | 84.6 | 83 | 80.6 | 78.8 | 73 | 67.3
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| B1FDBC03D43867B4355F8B6900BBC319XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\615A44RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:12:12
| End: | 2020-12-17, 23:12:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73.4 | 69.7 | 78.6 | 87.6 | 88.6 | 88.7 | 86.9 | 85.1 | 82.5 | 82.5 | 79.2 | 72.1
| LZFmin | 56.8 | 56.6 | 69.5 | 80.3 | 83.3 | 84.5 | 83.8 | 82.6 | 81 | 80.3 | 75.9 | 67
| LZeq | 66.2 | 63.6 | 74.4 | 83.9 | 86.1 | 86.4 | 85.6 | 83.9 | 81.7 | 81.4 | 77.2 | 68.9
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 8F2532D94D83421CF94B166683FD7890XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\617M40RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:13:12
| End: | 2020-12-17, 23:13:22
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68.4 | 68.7 | 77 | 85.2 | 87 | 88.8 | 87.5 | 85.1 | 82.9 | 81.8 | 76.5 | 74.2
| LZFmin | 52 | 52.9 | 67.8 | 77.4 | 81 | 84.7 | 83.7 | 82.3 | 81.2 | 80.3 | 74.9 | 71.7
| LZeq | 61.1 | 60.4 | 72.4 | 81.6 | 84 | 86.6 | 85.5 | 83.6 | 82 | 81.1 | 75.7 | 73
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 10ACC140B7834A199C35F0B7BEC50A43XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\619B33RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 23:14:18
| End: | 2020-12-17, 23:14:28
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 63.7 | 61.6 | 78.3 | 89.4 | 87.5 | 86.2 | 84.7 | 82.9 | 81.2 | 80.2 | 75 | 72
| LZFmin | 46.5 | 50.8 | 67.9 | 82.7 | 82.3 | 82.5 | 82.2 | 80.9 | 79.5 | 78.4 | 72.6 | 65
| LZeq | 56.5 | 57.2 | 74.2 | 86.3 | 85.2 | 84.3 | 83.7 | 82 | 80.4 | 79.3 | 73.6 | 68.8
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 285563203741EA0403CBA8278F62298CXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\632RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:57:22
| End: | 2020-12-17, 21:57:32
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 70 | 66.6 | 81.8 | 90.3 | 86.8 | 87.7 | 86.1 | 83.1 | 81.3 | 80.4 | 76 | 70.5
| LZFmin | 49.3 | 52 | 69.7 | 82.2 | 82.1 | 83.2 | 83 | 81.1 | 79.7 | 79 | 74.2 | 67
| LZeq | 63.2 | 58.8 | 75.9 | 86 | 84.7 | 85.6 | 84.4 | 82.1 | 80.5 | 79.8 | 75.2 | 68.8
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| F897458CA2066A1C65284F8C6A38BCD0XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\634RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:56:16
| End: | 2020-12-17, 21:56:26
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 73.4 | 70.2 | 76.9 | 86.2 | 86.5 | 88 | 86.1 | 83.9 | 81.8 | 80.5 | 76.5 | 70.3
| LZFmin | 55 | 54 | 67.5 | 78.4 | 82 | 84.1 | 83.3 | 81.2 | 80.3 | 79 | 74.9 | 67.8
| LZeq | 65.8 | 63.1 | 73.5 | 82.4 | 84.3 | 86 | 84.9 | 82.7 | 81 | 79.9 | 75.6 | 68.9
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| D05FB2A7BAFA4617C9EA32EC3CFB9C5EXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\636RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:55:28
| End: | 2020-12-17, 21:55:38
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 72.1 | 71.9 | 80.2 | 85.9 | 86.2 | 87.1 | 87.4 | 86.7 | 84.7 | 83.6 | 77.9 | 76.9
| LZFmin | 53.6 | 55 | 69.3 | 77 | 80.9 | 83.6 | 84.8 | 84.3 | 83 | 82.3 | 76.2 | 74.3
| LZeq | 64.1 | 64.9 | 74.9 | 81.5 | 83.7 | 85.4 | 86.1 | 85.5 | 83.8 | 82.9 | 77.2 | 75.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 766ADF91FFA3A0C5BE3087B3E4A2AD5AXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\638RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:54:36
| End: | 2020-12-17, 21:54:46
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 68.5 | 68.5 | 77.9 | 83.5 | 85.6 | 86.8 | 86.2 | 83.4 | 81.1 | 79.4 | 73 | 69.4
| LZFmin | 53.4 | 54.1 | 69 | 77.4 | 80.7 | 83 | 83.4 | 81.1 | 79.2 | 78.3 | 71.5 | 66.6
| LZeq | 61.8 | 60.6 | 73.4 | 80.8 | 83.2 | 84.7 | 84.7 | 82.3 | 80.3 | 78.8 | 72.2 | 67.7
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| BA2113B271AA42C0D42DAFFEEE924EABXL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\640RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:52:50
| End: | 2020-12-17, 21:53:00
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 63.9 | 66.2 | 79 | 86.2 | 88.1 | 88.2 | 84.1 | 82.5 | 80.3 | 79.1 | 74 | 66.6
| LZFmin | 48.9 | 51.2 | 66.5 | 78 | 82.4 | 84 | 81.5 | 80.8 | 78.4 | 77.7 | 72.3 | 63.4
| LZeq | 57.9 | 60.2 | 72.9 | 82 | 85.2 | 85.9 | 82.8 | 81.6 | 79.3 | 78.3 | 73.1 | 65
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| C2252335E79595B32098679845A2A8F7XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\642RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:52:04
| End: | 2020-12-17, 21:52:14
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 72 | 68.4 | 79.7 | 86.6 | 86.3 | 88.4 | 86.3 | 84 | 81.2 | 80 | 75.4 | 68.1
| LZFmin | 53.7 | 54.4 | 67.5 | 78.7 | 80.8 | 84.5 | 82.3 | 81.4 | 79 | 78 | 73 | 64.9
| LZeq | 62.7 | 63.6 | 75.1 | 83 | 83.6 | 86.4 | 84.2 | 82.4 | 79.9 | 78.9 | 74.3 | 66.4
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
| 6FAF1D9E1842446AD3B70D0FC59DBEB2XL2 Sound Level Meter RTA Reporting: |  | NST RTALVL6-2804\644RTA_SLM_000_RTA_Oct_Report.txt
------------------------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-02610-D1, FW4.50
| Mic Type: | NTi Audio M2230, SNo. 5215, User calibrated 2020-12-03 21:11
| Mic Sensitivity: | 45.5 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| Timer mode: | single
| Timer set: | 0:00
| Resolution: | 1/1 Octave
| Range: | 20 - 120 dB
# Time
| Start: | 2020-12-17, 21:49:28
| End: | 2020-12-17, 21:49:38
# RTA Results
| Band [Hz] | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
|  | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB] | [dB]
| LZFmax | 69 | 66.8 | 82.1 | 88.3 | 87.9 | 86.9 | 85.2 | 82.9 | 80.8 | 79.5 | 75.7 | 70.5
| LZFmin | 51.6 | 52.9 | 69.8 | 79.3 | 81.9 | 83.2 | 82.5 | 81.1 | 79 | 78.1 | 72.7 | 65
| LZeq | 61.2 | 60 | 74.7 | 84.7 | 84.5 | 85.1 | 83.9 | 81.9 | 79.9 | 78.9 | 74.4 | 67.5
| L_Capt | 47.2 | 53.8 | 72.8 | 81.1 | 77.9 | 72.6 | 71.5 | 70.3 | 69.3 | 66.1 | 62.2 | 52.1
#CheckSum
5414A274EEA8EBECFF5C623839189798

## Level 1 STI RAW
XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT123STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:58 | 2021-04-16 | 15:58 | 0.54 |  | 87.1 | OK |  | 87.7 | 0.33 | 0.27 | OK | 90 | 0.63 | 0.41 | OK | 86 | 0.71 | 0.43 | OK | 80.8 | 0.54 | 0.45 | OK | 75.4 | 0.67 | 0.58 | OK | 70.2 | 0.79 | 0.66 | OK | 60.8 | 0.79 | 0.52 | OK
#CheckSum
| 98144F6868FCADBA108A85E4C04CC091XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT127STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:56 | 2021-04-16 | 15:57 | 0.54 |  | 87.6 | OK |  | 90.6 | 0.85 | 0.58 | OK | 91.5 | 0.54 | 0.61 | OK | 86.4 | 0.81 | 0.52 | OK | 80.3 | 0.55 | 0.29 | OK | 74.5 | 0.6 | 0.52 | OK | 69 | 0.78 | 0.66 | OK | 59.7 | 0.77 | 0.64 | OK
#CheckSum
| A7711E37FB291A3AC229E0E57B4AEA9AXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT132STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:53 | 2021-04-16 | 15:54 | 0.43 |  | 86.3 | OK |  | 88.3 | 0.32 | 0.19 | OK | 90.3 | 0.42 | 0.38 | OK | 85.4 | 0.53 | 0.52 | OK | 78.8 | 0.4 | 0.14 | OK | 72.4 | 0.4 | 0.28 | OK | 66.6 | 0.63 | 0.47 | OK | 56 | 0.72 | 0.26 | OK
#CheckSum
| 15418DA5AFB816FF9B59120550CEE72BXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT135STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:49 | 2021-04-16 | 15:49 | 0.59 |  | 88 | OK |  | 90 | 0.72 | 0.59 | OK | 90.7 | 0.51 | 0.57 | OK | 87.8 | 0.82 | 0.7 | OK | 81.1 | 0.63 | 0.44 | OK | 75.9 | 0.73 | 0.64 | OK | 70.4 | 0.77 | 0.72 | OK | 59.5 | 0.88 | 0.45 | OK
#CheckSum
| 1027BDFB2BE24EB4FF2DF43123084AC2XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT137STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:48 | 2021-04-16 | 15:48 | 0.58 |  | 89.3 | OK |  | 89 | 0.66 | 0.38 | OK | 92.9 | 0.59 | 0.53 | OK | 88 | 0.73 | 0.88 | OK | 82.7 | 0.71 | 0.43 | OK | 76.6 | 0.71 | 0.6 | OK | 71.3 | 0.74 | 0.74 | OK | 62.1 | 0.91 | 0.43 | OK
#CheckSum
| 52CBCE3714DDCC31124143877A6B9363XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT139STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:18 | 2021-04-16 | 16:18 | 0.53 |  | 86.8 | OK |  | 89 | 0.51 | 0.38 | OK | 90.1 | 0.59 | 0.59 | OK | 85.9 | 0.69 | 0.67 | OK | 79.5 | 0.59 | 0.33 | OK | 74.5 | 0.59 | 0.5 | OK | 68.1 | 0.67 | 0.59 | OK | 58.9 | 0.88 | 0.37 | OK
#CheckSum
| D3AEF495EC7269C1DDE08096D61BB374XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT142STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:17 | 2021-04-16 | 16:17 | 0.57 |  | 86.9 | OK |  | 89.2 | 0.71 | 0.63 | OK | 89.1 | 0.39 | 0.38 | OK | 86.5 | 0.72 | 0.72 | OK | 80.1 | 0.58 | 0.53 | OK | 75.1 | 0.69 | 0.57 | OK | 69.9 | 0.78 | 0.68 | OK | 59.3 | 0.88 | 0.41 | OK
#CheckSum
| 51B2FAD622414BDB1C5BF329EA6EAE5DXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT144STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:15 | 2021-04-16 | 16:15 | 0.57 |  | 87.5 | OK |  | 89.2 | 0.57 | 0.45 | OK | 90.7 | 0.61 | 0.54 | OK | 86.5 | 0.6 | 0.66 | OK | 80.6 | 0.63 | 0.45 | OK | 74.5 | 0.7 | 0.6 | OK | 70.1 | 0.81 | 0.72 | OK | 60.1 | 0.89 | 0.39 | OK
#CheckSum
| 1C5FB51CE3D22E6DD1C639891F3C7C4DXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT145STITP_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:23 | 2021-04-16 | 16:23 | 0.4 |  | 85.1 | OK |  | 87.1 | 0.69 | 0.3 | OK | 89 | 0.49 | 0.31 | OK | 83.9 | 0.43 | 0.38 | OK | 77.8 | 0.38 | 0.07 | OK | 70.9 | 0.43 | 0.23 | OK | 65.9 | 0.63 | 0.4 | OK | 55.4 | 0.72 | 0.19 | OK
#CheckSum
| DA4467868C9D1EF8C0ABDC1355747BDDXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT149STIBM_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:11 | 2021-04-16 | 16:11 | 0.53 |  | 86.2 | OK |  | 88.2 | 0.57 | 0.25 | OK | 89.2 | 0.55 | 0.53 | OK | 85.4 | 0.71 | 0.6 | OK | 79.4 | 0.64 | 0.4 | OK | 73.2 | 0.57 | 0.4 | OK | 68.5 | 0.76 | 0.71 | OK | 57.3 | 0.83 | 0.4 | OK
#CheckSum
| 4B2EAD05B52FCC8CDE1BF0841457C4F5XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1NT149STITP_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:10 | 2021-04-16 | 16:11 | 0.46 |  | 84.4 | OK |  | 87.5 | 0.58 | 0.14 | OK | 88.1 | 0.57 | 0.58 | OK | 83.3 | 0.38 | 0.44 | OK | 77 | 0.45 | 0.24 | OK | 69.9 | 0.34 | 0.32 | OK | 66 | 0.69 | 0.62 | OK | 56.1 | 0.86 | 0.36 | OK
#CheckSum
| EEEB9577E0831C3CA2C3E2B0E8E1D566XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST102STIBM_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:08 | 2021-04-16 | 16:09 | 0.55 |  | 85.8 | OK |  | 87.9 | 0.57 | 0.17 | OK | 89.2 | 0.71 | 0.26 | OK | 84.1 | 0.59 | 0.5 | OK | 79.1 | 0.51 | 0.36 | OK | 74.4 | 0.72 | 0.61 | OK | 69.3 | 0.84 | 0.71 | OK | 57.9 | 0.85 | 0.51 | OK
#CheckSum
| 2AA90092BA75FEBB8E04A47451094245XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST102STITP_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:07 | 2021-04-16 | 16:08 | 0.45 |  | 84.1 | OK |  | 88.8 | 0.45 | 0.63 | OK | 88 | 0.58 | 0.49 | OK | 82.7 | 0.37 | 0.32 | OK | 76.9 | 0.51 | 0.25 | OK | 69.9 | 0.42 | 0.22 | OK | 65.9 | 0.67 | 0.64 | OK | 55.4 | 0.81 | 0.37 | OK
#CheckSum
| AE70B31396A5B566290D1DBF6C80867CXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST105STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:06 | 2021-04-16 | 16:06 | 0.49 |  | 84.7 | OK |  | 86.6 | 0.29 | 0.28 | OK | 87.4 | 0.46 | 0.4 | OK | 84.5 | 0.7 | 0.7 | OK | 77.2 | 0.52 | 0.23 | OK | 71.2 | 0.51 | 0.33 | OK | 65.8 | 0.61 | 0.5 | OK | 56 | 0.81 | 0.48 | OK
#CheckSum
| 76E7B3DB9B7C60A693A90BA92F4AC326XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST107STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:04 | 2021-04-16 | 16:04 | 0.57 |  | 87.1 | OK |  | 88.1 | 0.6 | 0.55 | OK | 89.8 | 0.33 | 0.43 | OK | 86 | 0.65 | 0.75 | OK | 81.1 | 0.7 | 0.52 | OK | 74.9 | 0.68 | 0.58 | OK | 69.3 | 0.76 | 0.71 | OK | 60 | 0.89 | 0.36 | OK
#CheckSum
| F07285CA2695A3CBA80A52D001DC6A67XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST109STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:03 | 2021-04-16 | 16:03 | 0.54 |  | 86.5 | OK |  | 86.8 | 0.49 | 0.39 | OK | 89.5 | 0.16 | 0.23 | OK | 84.9 | 0.56 | 0.57 | OK | 80.2 | 0.62 | 0.4 | OK | 74.6 | 0.63 | 0.61 | OK | 69.3 | 0.78 | 0.7 | OK | 59.4 | 0.91 | 0.31 | OK
#CheckSum
| 3897C0DB2079B58B2726C75F419E6766XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST112STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:02 | 2021-04-16 | 16:03 | 0.54 |  | 86.2 | OK |  | 88.2 | 0.49 | 0.59 | OK | 89.3 | 0.44 | 0.39 | OK | 85.1 | 0.63 | 0.65 | OK | 79.9 | 0.64 | 0.35 | OK | 73.4 | 0.57 | 0.53 | OK | 68.5 | 0.66 | 0.68 | OK | 58.4 | 0.88 | 0.61 | OK
#CheckSum
| BB024D570B553667E3339FD33E45DDDEXL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST114STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:01 | 2021-04-16 | 16:02 | 0.49 |  | 85.8 | OK |  | 89 | 0.49 | 0.64 | OK | 89.9 | 0.34 | 0.57 | OK | 84.6 | 0.56 | 0.55 | OK | 78.1 | 0.51 | 0.35 | OK | 72.1 | 0.34 | 0.4 | OK | 66.7 | 0.54 | 0.57 | OK | 57.2 | 0.88 | 0.7 | OK
#CheckSum
| 4F1D5BFBC1B6BD2AB228108EFC360622XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST117STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 16:00 | 2021-04-16 | 16:00 | 0.54 |  | 87 | OK |  | 88.6 | 0.4 | 0.43 | OK | 89.8 | 0.31 | 0.55 | OK | 86.2 | 0.71 | 0.59 | OK | 80.4 | 0.63 | 0.45 | OK | 74.9 | 0.54 | 0.56 | OK | 69.2 | 0.7 | 0.64 | OK | 59.9 | 0.88 | 0.53 | OK
#CheckSum
| ACE63BFF174558755BF72920BE630BB3XL2 STIPA Reporting: |  | NSTLVL1NORTHSTI\L1ST119STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 15:58 | 2021-04-16 | 15:59 | 0.56 |  | 87.2 | OK |  | 88.8 | 0.71 | 0.46 | OK | 89.4 | 0.48 | 0.48 | OK | 86.3 | 0.73 | 0.55 | OK | 81.3 | 0.68 | 0.45 | OK | 74.6 | 0.62 | 0.61 | OK | 70.4 | 0.81 | 0.73 | OK | 60.7 | 0.88 | 0.37 | OK
#CheckSum
E5537D9C6D7AFF054EC76F4665332B7E

## Level 4 STI RAW
XL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT431STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:52 | 2021-04-16 | 12:52 | 0.43 |  | 84.5 | OK |  | 87.2 | 0.55 | 0.4 | OK | 87.9 | 0.69 | 0.49 | OK | 83.5 | 0.68 | 0.43 | OK | 77.3 | 0.35 | 0.12 | OK | 71.1 | 0.36 | 0.21 | OK | 65.1 | 0.65 | 0.4 | OK | 55.8 | 0.68 | 0.37 | OK
#CheckSum
| F5AD3C2BE29C7B721EA43338C4CD5B3EXL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT435STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:47 | 2021-04-16 | 12:48 | 0.49 |  | 84.6 | OK |  | 86.1 | 0.48 | 0.5 | OK | 86.5 | 0.39 | 0.33 | OK | 83.2 | 0.45 | 0.5 | OK | 78.9 | 0.53 | 0.23 | OK | 73.8 | 0.55 | 0.47 | OK | 67.3 | 0.69 | 0.63 | OK | 57.4 | 0.8 | 0.25 | OK
#CheckSum
| 62F747C5DFC03EA32C77EE97340127A9XL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT437STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:42 | 2021-04-16 | 12:42 | 0.5 |  | 85.1 | OK |  | 85.7 | 0.46 | 0.17 | OK | 87.1 | 0.7 | 0.63 | OK | 83.6 | 0.53 | 0.46 | OK | 79.4 | 0.52 | 0.34 | OK | 74.5 | 0.55 | 0.38 | OK | 67.2 | 0.66 | 0.6 | OK | 57.6 | 0.82 | 0.4 | OK
#CheckSum
| 6B8ACADAB277CC047F9FA4925D5B0E57XL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT439STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:40 | 2021-04-16 | 12:40 | 0.38 |  | 85.2 | OK |  | 87.5 | 0.44 | 0.58 | OK | 87.9 | 0.35 | 0.2 | OK | 83.6 | 0.28 | 0.25 | OK | 79 | 0.28 | 0.08 | OK | 73.9 | 0.34 | 0.3 | OK | 67 | 0.49 | 0.41 | OK | 56.3 | 0.69 | 0.36 | OK
#CheckSum
| 13F353079C2F80BB285B7CC84B0DDB6AXL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT442STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:39 | 2021-04-16 | 12:39 | 0.47 |  | 86.4 | OK |  | 88.6 | 0.44 | 0.22 | OK | 88.6 | 0.39 | 0.41 | OK | 85.2 | 0.55 | 0.39 | OK | 80.3 | 0.48 | 0.21 | OK | 74.4 | 0.47 | 0.36 | OK | 70.5 | 0.75 | 0.65 | OK | 59.3 | 0.77 | 0.32 | OK
#CheckSum
| 455EB87125B47A772C0D784F968A20FFXL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\L4NT445STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:37 | 2021-04-16 | 12:38 | 0.53 |  | 87.3 | OK |  | 88.8 | 0.17 | 0.39 | OK | 88.5 | 0.4 | 0.2 | OK | 86.3 | 0.55 | 0.54 | OK | 81.6 | 0.56 | 0.38 | OK | 76.6 | 0.73 | 0.55 | OK | 70.8 | 0.77 | 0.65 | OK | 60.5 | 0.83 | 0.4 | OK
#CheckSum
| 3A3E98286EFE5595887758C00F8E518CXL2 STIPA Reporting: |  | NSTLVL4NORTHSTI\N4NTSCNSTI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:53 | 2021-04-16 | 12:53 | 0.57 |  | 86 | OK |  | 83.5 | 0.38 | 0.08 | OK | 90.2 | 0.81 | 0.72 | OK | 84 | 0.67 | 0.55 | OK | 79.3 | 0.71 | 0.33 | OK | 74.7 | 0.75 | 0.6 | OK | 69.6 | 0.87 | 0.73 | OK | 60 | 0.84 | 0.33 | OK
#CheckSum
| 759920FB2E1F897FE9D061E1FB28BAAEXL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST405STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:05 | 2021-04-16 | 13:05 | 0.49 |  | 85.7 | OK |  | 86.5 | 0.15 | 0.33 | OK | 87.9 | 0.52 | 0.31 | OK | 83.4 | 0.28 | 0.26 | OK | 80.6 | 0.59 | 0.27 | OK | 75.4 | 0.67 | 0.47 | OK | 69.1 | 0.8 | 0.66 | OK | 58.5 | 0.84 | 0.37 | OK
#CheckSum
| A3C8DBEDB8163F3F582E9106231809D0XL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST409STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:02 | 2021-04-16 | 13:03 | 0.46 |  | 86 | OK |  | 86.3 | 0.45 | 0.2 | OK | 88.5 | 0.6 | 0.63 | OK | 84.6 | 0.44 | 0.44 | OK | 80.1 | 0.52 | 0.16 | OK | 74.3 | 0.54 | 0.36 | OK | 67.5 | 0.6 | 0.49 | OK | 57.3 | 0.75 | 0.28 | OK
#CheckSum
| DD6D1AF1ADCD5E5D31559AA8AA2FCCC4XL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST412STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:01 | 2021-04-16 | 13:01 | 0.47 |  | 86.4 | OK |  | 87 | 0.11 | 0.1 | OK | 88 | 0.58 | 0.44 | OK | 84.6 | 0.47 | 0.41 | OK | 81.4 | 0.54 | 0.32 | OK | 75.7 | 0.62 | 0.4 | OK | 67.5 | 0.58 | 0.49 | OK | 58.5 | 0.8 | 0.25 | OK
#CheckSum
| 5F3E4219C7E3A3A96C070991A5CEE59BXL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST414STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:00 | 2021-04-16 | 13:00 | 0.46 |  | 86 | OK |  | 87.9 | 0.28 | 0.35 | OK | 86.7 | 0.24 | 0.33 | OK | 84.6 | 0.47 | 0.4 | OK | 80.6 | 0.53 | 0.21 | OK | 75.8 | 0.63 | 0.41 | OK | 68.5 | 0.65 | 0.51 | OK | 59.3 | 0.81 | 0.15 | OK
#CheckSum
| 8E6542A0B2FEB3C05C3B1EEFF9A42709XL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST416STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:58 | 2021-04-16 | 12:59 | 0.47 |  | 84.3 | OK |  | 83.5 | 0.47 | 0.21 | OK | 86.4 | 0.48 | 0.27 | OK | 82.9 | 0.49 | 0.41 | OK | 78.6 | 0.48 | 0.2 | OK | 73.1 | 0.56 | 0.41 | OK | 66.4 | 0.72 | 0.57 | OK | 56.3 | 0.75 | 0.2 | OK
#CheckSum
| 0C7A7D390C461DAEE6FDB9DDD4CB5FB9XL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST421STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:57 | 2021-04-16 | 12:57 | 0.51 |  | 85.2 | OK |  | 86.1 | 0.28 | 0.14 | OK | 86.4 | 0.49 | 0.17 | OK | 84.3 | 0.71 | 0.49 | OK | 80.1 | 0.7 | 0.27 | OK | 72.9 | 0.63 | 0.4 | OK | 67.7 | 0.74 | 0.57 | OK | 58.6 | 0.79 | 0.34 | OK
#CheckSum
| 31BE0D513B60359047AA97AB01348FEFXL2 STIPA Reporting: |  | NSTLVL4SOUTHSTI\N4ST423STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:56 | 2021-04-16 | 12:56 | 0.52 |  | 86.1 | OK |  | 88.3 | 0.68 | 0.38 | OK | 88.6 | 0.75 | 0.48 | OK | 85.3 | 0.76 | 0.53 | OK | 80.1 | 0.6 | 0.3 | OK | 73.6 | 0.67 | 0.38 | OK | 68.5 | 0.82 | 0.55 | OK | 59 | 0.75 | 0.14 | OK
#CheckSum
4B800B862144E6ECBAC004177E0FB21C

## Level 6 STI RAW
XL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT632STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:31 | 2021-04-16 | 12:31 | 0.53 |  | 86.6 | OK |  | 85.1 | 0.5 | 0.11 | OK | 87.7 | 0.53 | 0.41 | OK | 86.2 | 0.78 | 0.72 | OK | 80.9 | 0.64 | 0.22 | OK | 74.3 | 0.72 | 0.43 | OK | 69 | 0.79 | 0.54 | OK | 59.6 | 0.67 | 0.47 | OK
#CheckSum
| 6841130B710059F9A11D974FE062F28FXL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT634STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:29 | 2021-04-16 | 12:29 | 0.57 |  | 86.7 | OK |  | 86.2 | 0.79 | 0.11 | OK | 88.4 | 0.5 | 0.41 | OK | 85 | 0.68 | 0.73 | OK | 81.1 | 0.66 | 0.55 | OK | 75.6 | 0.74 | 0.49 | OK | 71.8 | 0.87 | 0.67 | OK | 60.3 | 0.69 | 0.52 | OK
#CheckSum
| DD1B65EF63A9C13D2AFB7A1F923EC79EXL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT636STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:30 | 2021-04-16 | 12:30 | 0.63 |  | 85.5 | OK |  | 84.7 | 0.85 | 0.81 | OK | 86.9 | 0.72 | 0.44 | OK | 84.5 | 0.78 | 0.6 | OK | 80.3 | 0.85 | 0.61 | OK | 74 | 0.8 | 0.62 | OK | 68.2 | 0.86 | 0.6 | OK | 59.9 | 0.82 | 0.7 | OK
#CheckSum
| 87043383B0E0760C5A0AB54A7EDBE2CBXL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT638STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:28 | 2021-04-16 | 12:28 | 0.54 |  | 87.1 | OK |  | 83.5 | 0.6 | 0.24 | OK | 89.6 | 0.44 | 0.48 | OK | 85.9 | 0.72 | 0.59 | OK | 81.3 | 0.63 | 0.43 | OK | 75.6 | 0.7 | 0.58 | OK | 70 | 0.75 | 0.54 | OK | 59.1 | 0.59 | 0.39 | OK
#CheckSum
| CF62CB52C0E8B5C92012C600EA69C68BXL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT638STI_STIPA_001_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:29 | 2021-04-16 | 12:29 | 0.57 |  | 86.7 | OK |  | 86.2 | 0.79 | 0.11 | OK | 88.4 | 0.5 | 0.41 | OK | 85 | 0.68 | 0.73 | OK | 81.1 | 0.66 | 0.55 | OK | 75.6 | 0.74 | 0.49 | OK | 71.8 | 0.87 | 0.67 | OK | 60.3 | 0.69 | 0.52 | OK
#CheckSum
| 01CABB9487BA0CCCB51BBC04DA367F95XL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT640STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:27 | 2021-04-16 | 12:27 | 0.59 |  | 84.1 | OK |  | 83.8 | 0.88 | 0.55 | OK | 85.5 | 0.7 | 0.51 | OK | 83.3 | 0.82 | 0.65 | OK | 78.4 | 0.7 | 0.45 | OK | 72.6 | 0.75 | 0.54 | OK | 66.6 | 0.85 | 0.56 | OK | 56.9 | 0.73 | 0.45 | OK
#CheckSum
| D2D1AB05E8871C85084D612125F081A9XL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT642STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:26 | 2021-04-16 | 12:26 | 0.61 |  | 85.5 | OK |  | 83.8 | 0.75 | 0.24 | OK | 87.7 | 0.67 | 0.61 | OK | 84.3 | 0.78 | 0.76 | OK | 80 | 0.75 | 0.49 | OK | 73.5 | 0.82 | 0.58 | OK | 69.4 | 0.83 | 0.73 | OK | 58.9 | 0.79 | 0.6 | OK
#CheckSum
| D709853665B1C12E0E9E701A4BE09835XL2 STIPA Reporting: |  | NSTLVL6NORTHSTI\L6NT644STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 12:24 | 2021-04-16 | 12:24 | 0.51 |  | 85.8 | OK |  | 86.6 | 0.25 | 0.1 | OK | 86.7 | 0.5 | 0.21 | OK | 84.5 | 0.65 | 0.37 | OK | 80.4 | 0.54 | 0.3 | OK | 75 | 0.67 | 0.48 | OK | 70.7 | 0.78 | 0.6 | OK | 60.8 | 0.66 | 0.58 | OK
#CheckSum
| 913E7DBA92E8965631FF9C5B8EEC81A4XL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST608STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:09 | 2021-04-16 | 13:10 | 0.52 |  | 86.9 | OK |  | 87 | 0.61 | 0.24 | OK | 89.6 | 0.72 | 0.27 | OK | 84.1 | 0.49 | 0.29 | OK | 81.9 | 0.62 | 0.44 | OK | 75.5 | 0.67 | 0.47 | OK | 71.1 | 0.82 | 0.61 | OK | 62 | 0.76 | 0.61 | OK
#CheckSum
| C9ED252BD8F24CA948118AA3810E811BXL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST609STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:11 | 2021-04-16 | 13:11 | 0.64 |  | 87.3 | OK |  | 88.9 | 1.06 | 0.75 | OK | 88.9 | 0.8 | 0.59 | OK | 86.4 | 0.89 | 0.75 | OK | 81.9 | 0.79 | 0.62 | OK | 75.7 | 0.78 | 0.62 | OK | 71 | 0.91 | 0.68 | OK | 61.1 | 0.82 | 0.61 | OK
#CheckSum
| 289A30CFC4DF74EF0ED92C3183FA67C3XL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST611STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:12 | 2021-04-16 | 13:12 | 0.6 |  | 85.4 | OK |  | 84.2 | 0.69 | 0.28 | OK | 88.4 | 0.92 | 0.55 | OK | 83.8 | 0.85 | 0.74 | OK | 79.6 | 0.76 | 0.53 | OK | 73.8 | 0.8 | 0.53 | OK | 68.5 | 0.85 | 0.62 | OK | 58.2 | 0.69 | 0.41 | OK
#CheckSum
| F8FF16D9889A73645634F46CF2F37B07XL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST613STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:13 | 2021-04-16 | 13:13 | 0.55 |  | 83.9 | OK |  | 80.6 | 0.68 | 0.35 | OK | 85.6 | 0.61 | 0.54 | OK | 83 | 0.73 | 0.53 | OK | 78.4 | 0.66 | 0.52 | OK | 72.2 | 0.66 | 0.49 | OK | 67.2 | 0.79 | 0.55 | OK | 56.6 | 0.66 | 0.48 | OK
#CheckSum
| 874153C2875D29ECA806D0EFD013F4BAXL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST615STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:14 | 2021-04-16 | 13:14 | 0.58 |  | 84.7 | OK |  | 83.8 | 0.76 | 0.41 | OK | 87.1 | 0.65 | 0.58 | OK | 82.9 | 0.71 | 0.65 | OK | 79.6 | 0.74 | 0.54 | OK | 73.1 | 0.71 | 0.53 | OK | 68.1 | 0.84 | 0.62 | OK | 57.1 | 0.7 | 0.51 | OK
#CheckSum
| DF49FB8D59A1B257804E30ED7E9CA267XL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST617STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:15 | 2021-04-16 | 13:15 | 0.63 |  | 86.1 | OK |  | 85.6 | 0.8 | 0.17 | OK | 87.5 | 0.86 | 0.54 | OK | 85.1 | 0.83 | 0.6 | OK | 80.3 | 0.78 | 0.54 | OK | 74.9 | 0.81 | 0.7 | OK | 69.9 | 0.93 | 0.68 | OK | 60.7 | 0.81 | 0.65 | OK
#CheckSum
| 2EB78D029215CDEF57F0C536C2BE6302XL2 STIPA Reporting: |  | NSTLVL6SOUTHSTI\N6ST619STI_STIPA_000_Report.txt
--------------------
# Hardware Configuration
| Device Info: | XL2, SNo. A2A-15893-E0, FW4.50
| Mic Type: | NTi Audio M4261, SNo. 2364, User calibrated 2020-12-07 14:30
| Mic Sensitivity: | 15.8 mV/Pa
| Time Zone: | UTC+08:00 (Asia/Singapore)
# Measurement Setup
| Profile: | Full mode
| Append mode: | OFF
| IEC 60268-16: | ed5.0 2020
# Ambient Noise to add
| Set Method: | measured
| Set Time: | 2021-03-31, 17:58
| LAeq [dB] | 50.6
| Band [Hz] | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
| LZeq [dB] | 52 | 51.2 | 47.9 | 46.3 | 41.4 | 34.2 | 24.8
# STIPA Results
STIPA results are reported with noise added.
LZeq, mr1 and mr2 results are the purely measured values.
| Start |  | Stop | [5 empty] | Band [Hz] | 125 |  |  |  | 250 |  |  |  | 500 |  |  |  | 1000 |  |  |  | 2000 |  |  |  | 4000 |  |  |  | 8000
| Date | Time | Date | Time | STIPA | CYCLE | LAeq | Status |  | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status | LZeq | mr1 | mr2 | Status
| [YYYY-MM-DD] | [hh:mm:ss] | [YYYY-MM-DD] | [hh:mm:ss] | [STI] | [STI] | [dB] |  |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1] |  | [dB] | [x1] | [x1]
| 2021-04-16 | 13:16 | 2021-04-16 | 13:16 | 0.53 |  | 85.7 | OK |  | 85.9 | 0.42 | 0.27 | OK | 84.6 | 0.17 | 0.14 | OK | 83.9 | 0.53 | 0.33 | OK | 81.6 | 0.65 | 0.46 | OK | 75.2 | 0.68 | 0.51 | OK | 71.1 | 0.81 | 0.62 | OK | 61.2 | 0.71 | 0.62 | OK
#CheckSum
2D03155C440AE637B3DE1E35C5ECA8D3